FIRE ALARM TEST – use the fire alarm control panel in the main entrance lobby.

AUXILIARY CONTROL PANELS in the meeting room lobby and social room are for fire service use only – no checks req’d.

To reduce the time the alarm sounds during testing ideally 2 people are required.

- Person 1 stands at the Fire alarm Control Panel ready to key in alt 514 , followed by button 1 silence alarm, followed by  button 2 reset alarm as soon as the alarm is triggered.

- Person 2 visits a call point (break glass point) to insert and turn ¼ turn clockwise a plastic test key as shown into the provided keyhole in the break glass point casing. The alarm will sound if the test is a “satisfactory”.

Test one call point per week so all 5 get tested at least once every 5 weeks. Note there are 2 call points in Zone 1

See Fire Safety Procedure document for Location of Call Points. Close both roller shutters before testing

DOOR RELEASE TEST

Activate and check for “satisfactory” operation, the “push to release” bar on each of the 5 emergency exits.

SMOKE & HEAT DETECTORS are tested 6-monthly by outside contractors

| DATE | FIRE ALARM | DOOR RELEASES | REMEDIAL ACTION TAKEN | NAME AND/OR ORGANISATION OF PERSON CARRYING OUT TEST |
| --- | --- | --- | --- | --- |
|  | CALL POINT No. | SATISFACTORY YES/NO | SATISFACTORY YES/NO |  |  |