## Sheet1
Client -Rowney Green Peace Hall, Rowney Green Lane, Rowney Green. B48 7QP | [5 empty] | Test Gear | PAT 320
[6 empty] | Serial No. | No.1000740101721560
[6 empty] | Tester | Paul Chadderton
[6 empty] | Date | 19.8.20
Signed
Asset | Description | Voltage | Class | Earth | Ins. | Protective/ | VA | RCD |  | PASS/ | Date of
ID |  |  |  | Bond | Res. | Touch Current |  | x1 | x5 | FAIL | next test
A7 | Bosch Kettle | 230V | I | 0.04 | 99.9 | 0.1 | 2667 |  |  | PASS | 2021-08-01
A8 | Bosch Kettle | 230V | I | 0.03 | 99.9 | 0.1 | 2751 |  |  | PASS | 2021-08-01
A9 | Henrietta vac | 230V | II |  | 99.9 |  | 639 |  |  | PASS | 2021-08-01
A10 | Dyson vac | 230V | II |  | 99.9 |  | 1436 |  |  | PASS | 2021-08-01
A11 | 16A-4x13A sockets | 230V | I | 0.09 | 99.9 |  |  |  |  | PASS | 2021-08-01
A12 | Marshall Amplifier | 230V | I | 0.06 | 99.9 | 0.1 | 9 |  |  | PASS | 2021-08-01
A13 | Snow man | 230V | II |  | 99.9 |  | 13 |  |  | PASS | 2021-08-01
A17 | 3 way 16A splitter | 230V | I | 0.03 | 99.9 |  |  |  |  | PASS | 2021-08-01
A20 | Display Screen | 230V | II |  | 99.9 | 10 |  |  |  | PASS | 2021-08-01
A26 | Slow cooker | 230V | I | 0.04 | 99.9 | 0.1 | 281 |  |  | PASS | 2021-08-01
A27 | Fairylight transformer | 230V | II |  | 99.9 |  | 3 |  |  | PASS | 2021-08-01
A31 | Warmer | 230V | I | 0.12 | 6.7 | 0.11 | 397 |  |  | PASS | 2021-08-01
A32 | Hearing Loop Transformer | 230V | II |  | 99.9 |  | 7 |  |  | PASS | 2021-08-01
A34 | Fairylight transformer | 230V | II |  | 99.9 |  | 7 |  |  | PASS | 2021-08-01
A36 | Fairylight transformer | 230V | II |  | 99.9 |  | 9 |  |  | PASS | 2021-08-01
A38 | Fairylight transformer | 230V | II |  | 99.9 |  | 8 |  |  | PASS | 2021-08-01
A39 | Fairylight transformer | 230V | II |  | 99.9 |  | 0 |  |  | PASS | 2021-08-01
A40 | Fairylight transformer | 230V | II |  | 99.9 |  | 3 |  |  | PASS | 2021-08-01
A41 | Fairylight transformer | 230V | II |  | 99.9 |  | 13 |  |  | PASS | 2021-08-01
A43 | Fairylight transformer | 230V | II |  | 99.9 |  | 8 |  |  | PASS | 2021-08-01
A44 | Fairylight transformer | 230V | II |  | 99.9 |  | 5 |  |  | PASS | 2021-08-01
A46 | Fairylight transformer | 230V | II |  | 99.9 |  | 6 |  |  | PASS | 2021-08-01
A92 | Outside tree lights | 230V | II |  | 99.9 |  | 0 |  |  | PASS | 2021-08-01
A93 | Outside tree lights | 230V | II |  | 99.9 |  | 0 |  |  | PASS | 2021-08-01
A96 | Fairylight transformer | 230V | II |  | 99.9 |  | 7 |  |  | PASS | 2021-08-01
A97 | 4 Way Tree adaptor | 230V | I | 0.06 | 99.9 |  |  |  |  | PASS | 2021-08-01
A127 | Desk Lamp | 230V | II |  | 99.9 |  | 20 |  |  | PASS | 2021-08-01
A128 | Desk Lamp | 230V | II |  | 99.9 |  | 22 |  |  | PASS | 2021-08-01
A165 | 4 way short extn | 230V | I | 0.05 | 99.9 |  |  |  |  | PASS | 2021-08-01
A166 | Slow cooker | 230V | I | 0.05 | 99.9 | 0.1 | 268 |  |  | PASS | 2021-08-01
A167 | Slow cooker | 230V | I | 0.05 | 99.9 | 0.1 | 311 |  |  | PASS | 2021-08-01
A168 | Slow cooker | 230V | I | 0.05 | 99.9 | 0.1 | 283 |  |  | PASS | 2021-08-01
A169 | Slow cooker | 230V | I | 0.04 | 99.9 | 0.1 | 254 |  |  | PASS | 2021-08-01
A171 | Beer chiller | 230V | I | 0.07 | 99.9 | 0.1 | 416 |  |  | PASS | 2022-08-01
A173 | 15m 10A Extn Lead | 230V | I | 0.32 | 99.9 |  |  |  |  | PASS | 2021-08-01
A196 | Fairylight transformer | 230V | II |  | 99.9 |  | 0 |  |  | PASS | 2021-08-01
A204 | Fairylight transformer | 230V | II |  | 99.9 |  | 10 |  |  | PASS | 2021-08-01
A205 | Fairylight transformer | 230V | II |  | 99.9 |  | 9 |  |  | PASS | 2021-08-01
A206 | Short extn | 230V | I | 0.03 | 99.9 |  |  |  |  | PASS | 2021-08-01