## Full Register
Asset ID | Location | Asset Description | Advised Test Frequency (months) | Date of Last PAT Test | If Different - Date Visually Inspected & Assessesed for Next Test | Testing policy (e.g. hours and frequency of use, durability of appliance, disturbance of appliance during or in between uses. Rating of Appliance (e.g. High power appliances - cables are subject to higher load than for low power appliances) etc. Spring 2015 policy amendment - items marked "Fixed Appliance" are no longer required to be tested (they are all protected by a circuit breaker and are not "portable") Power pack transformers e.g. for fairy lights, only required to have a "visual test" for cracks and/or other damage. The cable beyond the transformer is low voltage - not a safety hazard. | Name(s) of person/people Assessing for Frequency of PAT Testing | Asset VA | Operating Voltage | Fuse Rating | Earth Bond -Ohms | Insulation (Meg Ohms) | VA | Leak mA | Lead Condition | Result -(Pass/Fail)
Column1 | Column2 | Column3 | Column4 | Column5 | Column15 | Column17 | Column16 | Column7 | Column8 | Column9 | Column10 | Column11 | Column12 | Column13 | Column6 | Column14
A1 | MH Kitchen | Dishwasher | N/A | 17.7.19 |  | Estimated use = 2h/week = 100h/annun Suggest test every 2-3 years - Fixed Appliance | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Not Tested
A39 | Social Room Loft | Fairy Lights | 12 | 19.8.20 |  | Estimated use = .25h/week = 12h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | N/A | 99.9 | 0 |  | OK | Pass
A27 | Social Room Loft | Fairy lanterns | 12 | 19.8.20 |  | Estimated use = .25h/week = 12h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | N/A | 99.9 | 3 |  | OK | Pass
A96 | Social Room Loft | Fairy lanterns | 12 | 19.8.20 |  | Estimated use = .25h/week = 12h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | N/A | 99.9 | 7 |  | OK | Pass
A12 | Corridor Store | Marshall Amplifier | 12 | 19.8.20 |  | Estimated use = 2h/week = 100h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.06 | 99.9 | 9 | 0.1 | OK | Pass
A13 | Corridor Store | Xmas Snowman |  | 19.8.20 | [6 empty] | N/A | 99.9 | 13 |  | OK | Pass
A169 | Corridor Store | Slow Cooker | 12 | 19.8.20 |  | Estimated use = .25h/week = 12h/annun Suggest test every 2-3 years |  |  |  | 3 | 0.04 | 99.9 | 254 | 0.1 |  | Pass
A166 | Corridor Store | Slow Cooker | 12 | 19.8.20 |  | Estimated use = .25h/week = 12h/annun Suggest test every 2-3 years |  |  |  | 3 | 0.05 | 99.9 | 268 | 0.1 |  | Pass
A26 | Corridor store | Slow Cooker | N/A | 19.8.20 |  |  | Andrew May + Tony Cowles |  | 230 |  | 0.04 | 99.9 | 281 | 0.1 |  | Pass
A168 | Corridor Store | Slow Cooker | 12 | 19.8.20 |  | Estimated use = .25h/week = 12h/annun Suggest test every 2-3 years |  |  |  | 3 | 0.05 | 99.9 | 283 | 0.1 |  | Pass
A167 | Corridor Store | Slow Cooker | 12 | 19.8.20 |  | Estimated use = .25h/week = 12h/annun Suggest test every 2-3 years |  |  |  | 3 | 0.05 | 99.9 | 311 | 0.1 | OK | Pass
A31 | Janitorial Store | Echo Hostess | 12 | 19.8.20 |  | Estimated use = .25h/week = 12h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | 3 | 0.12 | 6.7 | 397 | 0.11 | OK | Pass
A9 | Janitorial Store | Henrietta Vac | 12 | 19.8.20 |  | Estimated use = 2h/week = 100h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | 13 | D/Inslulated | 99.9 | 639 |  | OK | Pass
A11 | Rear corridor store | 16A Plug to 2 x 13A converter lead | 12 | 19.8.20 |  | Estimated use = .25h/week = 12h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.09 | 99.9 |  |  | OK | Pass
A7 | MH Kitchen | Electric Kettle | 12 | 19.8.20 |  | Estimated use = 2h/week = 100h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | 13 | 0.04 | 99.9 | 2667 | 0.1 | OK | Pass
A8 | Rear Corridor | Electric Kettle | 12 | 19.8.20 |  | Estimated use = 2h/week = 100h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | 13 | 0.03 | 99.9 | 2751 | 0.1 | OK | Pass
A10 | Janitorial Store | Dyson Vac | 12 | 19.8.20 |  | Estimated use = 2h/week = 100h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | 13 | D/Inslulated | 99.9 | 1436 |  | OK | Pass
A99 | Stage | HDMI Booster | 24 | 17.7.19 | [7 empty] | 99.9 | 0 |  |  | Pass
A100 | Lighting Loft Extras | 400W UV Light | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.18 | 99.9 |  |  | OK | Missing
A101 | Lighting Loft Extras | Bifocal Spot | 12 | 17.7.19 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  |  | 99.9 | 48 |  | OK | Pass
A102 | Lighting Loft Extras | Effects Projector | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.16 | 99.9 |  |  | OK | Missing
A103 | Lighting Loft Extras | Soundlabs Smoke Machine | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.08 | 99.9 |  |  | OK | Pass
A118 | Front of House Lighting Rail | Mirror Ball Disc | 36 | 24.5.17 |  | Estimated use = .8h/week = 40h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | N/A | 0.09 | 999 |  |  | OK | Pass
A119 | Front of House Lighting Rail | Mirror Ball Light | 36 | 24.5.17 |  | Estimated use = .8h/week = 40h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.01 | 999 |  |  | OK | Pass
A104 | Lighting Loft Extras | Neon Smoke Machine | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.1 | 74.38 |  |  | OK | Missing
A120 | Front of House Lighting Rail | Mirror Ball Light | 36 | 24.5.17 |  | Estimated use = .8h/week = 40h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.01 | 999 |  |  | OK | Pass
A121 | Front of House Lighting Rail | Mirror Ball Disc | 36 | 24.5.17 |  | Estimated use = .8h/week = 40h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.01 | 999 |  |  | OK | Pass
A105 | Lighting Loft Extras | Bubble Machine | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.08 | 99.9 |  |  | OK | Missing
A123 | Stage | Digital Projector | 24 | 17.7.19 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.31 | 99.9 |  |  | OK | Pass
A125 | Stage | Fold-Back Speakers | 24 | 17.7.19 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | 5 | 0.32 | 99.9 | 10 |  | OK | Pass
A126 | Stage | Amplifier | 24 | 17.7.19 |  | Estimated use = 2h/week = 100h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | 13 | 0.32 | 99.9 | 6 | 0.1 | OK | Pass
A127 | Stage | Desk Lamp | 12 | 19.8.20 | [6 empty] | N/A | 99.9 | 20 |  | OK | Pass
A128 | Stage | Desk Lamp | 24 | 19.8.20 |  | Estimated use = 2h/week = 100h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | 3 | N/A | 99.9 | 22 |  | OK | Pass
A129 | Stage | Trailing Lead for digital Projector | 24 | 17.7.19 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | 13 | 0.2 | 99.9 |  |  | OK | Pass
A106 | Lighting Loft Extras | Sound Mixing Desk | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Missing
A130 | Stage | Projector Screen Controller | 24 | 17.7.19 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | 13 | N/A | 99.9 | 112 |  | OK | Pass
A107 | Lighting Loft Extras | Sound Computer | 36 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Missing
A108 | Lighting Loft Extras | Computer Monitor | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.09 | 99.9 |  |  | OK | Pass
A109 | Lighting Loft Extras | Light Control Power Supply Unit | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.08 | 99.9 | 3 |  | OK | Pass
A110 | Lighting Loft Extras | Main Hall Amplifier | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.07 | 99.9 |  |  | OK | Pass
A111 | Lighting Loft Extras | Tecpro Talkback System | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years - | Andrew May + Tony Cowles |  | 230 |  | 0.1 | 99.9 |  |  | OK | Pass
A112 | Lighting Loft Extras | Desk Lamp | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Missing
A113 | Lighting Loft Extras | Radio Microphone | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  |  | 99.9 | 4 |  | OK | Pass
A114 | Lighting Loft Extras | Video Link Recorder | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  |  | 99.9 | 0 |  | OK | Pass
A115 | Lighting Loft Extras | Fan | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.09 | 99.9 | 135 |  | OK | Pass
A116 | Lighting Loft Extras | Large freestanding spotlamp | 24 | 17.7.19 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.1 | 99.9 | 0 | 0.1 |  | Pass
A14 | Corridor Store | Smoothing Iron | N/A | 2011-12-01 |  | Stage Prop - not in use | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK
A117 | Lighting Loft Extras | Port Dimmer Unit | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
A122 | Front of House Lighting Rail | Camera | 36 | 21.6.18 |  | Changed to A181 | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Missing
A130 | Lighting Loft Cables | 6400mm Trailing Lead | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
A131 | Lighting Loft Cables | 6300mm Trailing Lead | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
A132 | Lighting Loft Cables | 8000mm Trailing Lead | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
A133 | Lighting Loft Cables | 8400mm Trailing Lead | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
A134 | Lighting Loft Cables | 4900mm Trailing Lead | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
A135 | Lighting Loft Cables | 6900mm Trailing Lead | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Missing
A136 | Lighting Loft Cables | 6800mm Trailing Lead | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Missing
A137 | Lighting Loft Cables | Short Trailing Lead | 24 | 17.7.19 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.1 | 99.9 |  |  | OK | Pass
A15 | SR Loft | Table Lamp | 24 | 19.8.20 |  | Stage Prop - not in use | Andrew May + Tony Cowles |  | 230 |  | 0.12 | 999 |  |  | OK | 2020 removed
A138 | Lighting Loft Cables | Short Trailing Lead | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.06 | 99.9 |  |  | OK | Missing
A139 | Lighting Loft Cables | Short Trailing Lead | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.04 | 99.9 |  |  | OK | Pass
A140 | Lighting Loft Cables | 2400mm Trailing Lead | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Missing
A141 | Lighting Loft Cables | 7900mm Trailing Lead | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
A142 | Lighting Loft Cables | 10700mm Trailing Lead | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Missing
A143 | Lighting Loft Cables | 5000mm Trailing Lead | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Missing
A144 | Lighting Loft Cables | 3100mm Trailing Lead | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
A145 | Lighting Loft Cables | 6000mm Trailing Lead | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Missing
A146 | Lighting Loft Cables | 5030mm Trailing Lead | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
A147 | Lighting Loft Cables | Short Trailing Lead | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
A16 | SR Loft | Table Lamp | 24 | 19.8.20 |  | Stage Prop - not in use | Andrew May + Tony Cowles |  | 230 | 3 | N/A | 999 |  |  | OK | 2020 removed
A148 | Lighting Loft Cables | Short Trailing Lead | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
A149 | Lighting Loft Cables | 1400mm Trailing Lead | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
A150 | Lighting Loft Cables | Short Trailing Lead | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
A151 | Lighting Loft Cables | Short Trailing Lead | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
A152 | Lighting Loft Cables | Short Trailing Lead | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
A165 | On-Stage | Multiblock Extension | 24 | 19.8.20 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | 13 | 0.05 | 99.9 |  |  | OK | Pass
A153 | Lighting Loft Cables | Short Trailing Lead | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
A154 | Lighting Loft Cables | 2000mm Trailing Lead | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
A155 | Lighting Loft Cables | 1800mm Trailing Lead | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
A156 | Lighting Loft Cables | 2000mm Trailing Lead | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Missing
A157 | Lighting Loft Cables | 2000mm Trailing Lead | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
A158 | Lighting Loft Cables | 3100mm Trailing Lead | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
A159 | Lighting Loft Cables | 3200mm Trailing Lead | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
A160 | Lighting Loft Cables | 5200mm Trailing Lead | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Missing
A17 | Corridor Store | 16A 3 way Splitter | 12 | 19.8.20 |  |  | Andrew May + Tony Cowles |  | 230 | N/A | 0.03 | 99.9 |  |  | OK | Pass
A170 | Rear corridor | Beer chiller | 24 | 17.7.19 | [5 empty] | 5 | 0.09 | 99.9 | 445 | 0.1 |  | Pass
A171 | Rear corridor | Spare Beer Chiller | 24 | 17.7.19 | [5 empty] | 5 | 0.07 | 99.9 | 428 | 0.1 |  | Pass
A172 | Corridor Store | Beer chiller | 24 | 17.7.19 | [5 empty] | 13 | 0.14 | 99.9 | 269 | 0.1 |  | Pass
A173 | Corridor Store | 15m 10A Extension Cable Reel | 12 | 19.8.20 |  | Estimated use = .25h/week = 12h/annun Suggest test every 2-3 years |  |  |  | 10 | 0.32 | 99.9 |  |  | OK | Pass
A174 | Front of House Lighting Rail | 600mm Trailing Lead | 36 | 24.5.17 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years |  |  |  | N/A | 0.01 | 999 |  |  |  | Pass
A2 | MH Kitchen | Water Descaler | N/A | 2015-02-18 |  | Estimated use = 2h/week = 100h/annun Suggest test every 2-3 years - Fixed Appliance | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Not Tested
A37 | MH Kitchen | Kitchen roller shutter | 24 | 17.7.19 | [6 empty] | 0.1 | 99.9 | 12 | 0.24 |  | Pass
A98 | G&T | G&T roller shutter | 24 | 17.7.19 | [6 empty] | 0.09 | 77.58 | 15 | 0.21 |  | Pass
A20 | Stored here when not in use | Display Screen | 24 | 19.8.20 | [6 empty] | N/A | 99.9 | 10 |  | OK | Pass
A21 | SR Kitchen | Fracino Coffee Machine | 24 | 17.7.19 |  | Estimated use = 2.5h/week = 150h/annun Suggest test every 2-3 years - Fixed appliance | Andrew May + Tony Cowles |  | 230 | 13 | 0.07 | 99.9 | 2754 | 0.1 | OK | Pass
A22 | Social Room Kitchen | Display Fridge | 24 | 17.7.19 |  | 24/7 - not moved - Suggest test every 2-3 years - Fixed appliance | Andrew May + Tony Cowles |  | 230 | 13 | 0.1 | 99.9 |  | 0.1 | OK | Pass
A23 | Social Room Kitchen | Normal Fridge | 24 | 17.7.19 |  | 24/7 - not moved - Suggest test every 2-3 years - Fixed appliance | Andrew May + Tony Cowles |  | 230 | 13 | 0.09 | 99.9 |  | 0.1 | OK | Pass
A24 | Social Room Kitchen | Glass Washer | 24 | 17.7.19 |  | Estimated use = 2h/week = 100h/annun Suggest test every 2-3 years - Fixed appliance | Andrew May + Tony Cowles |  | 230 | 13 | 0.06 | 99.9 |  | 0.1 | OK | Pass
A161 | Lighting Loft Cables | Short Trailing Lead | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Missing
A162 | Lighting Loft Cables | Short Trailing Lead | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.09 | 99.9 |  |  | OK | Pass
A163 | Lighting Loft Cables | Short Trailing Lead | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Missing
A28 | Meeting Room Loft | Electrolux Vac | N/A | not in use |  | Stage Prop - not in use | Andrew May + Tony Cowles |  | 230
A29 | Meeting Room Loft | Desk Lamp | N/A | not in use |  | Stage Prop - not in use | Andrew May + Tony Cowles |  | 230
A3 | MH Kitchen | Plinth Heater | N/A | 2015-02-18 |  | Estimated use = 4h/week = 200h/annun Suggest test every 2-3 years - Fixed Appliance | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Not Tested
A30 | Meeting Room Loft | Desk Lamp | N/A | not in use |  | Stage Prop - not in use | Andrew May + Tony Cowles |  | 230
A164 | Lighting Loft Cables | Short Trailing Lead | 24 | 17.7.19 |  | Cable join issue to strobe asset A183, deleted | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Deleted
A202 | Lighting Loft Cables | Extension Cable Reel | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
A203 |  | Wall Mounted Dell Monitor | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.17 | 99.9 |  |  | OK | Pass
???? | Duplicate A167 | Radio Switch | 24 | 21.6.18 |  | Duplicate Asset no A167 with Slow Cooker. Tried to re-number as A204 but couldn't find the Asset. Needs clarification but probably doesn't exist. | Andrew May + Tony Cowles |  | 230 |  | 0.01 | 99.9 |  |  | OK | Item not found
A200 |  | Radio Switch | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years - Visual Test Only | Andrew May + Tony Cowles |  | 230 |  | 0.01 | 99.9 |  |  | OK | Pass
A36 | Social room loft | 2m extension lead | N/A | 19.8.20 |  |  | Andrew May + Tony Cowles |  | 230 |  | N/A | 99.9 | 9 |  | OK | Pass
A25 | Social Room Kitchen | Intempo Music Player | 12 | 19.8.20 |  | Visual Test only | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Delete - off site
A33 | Stored here when not in use | Fairy Lights | 12 | 19.8.20 |  | Visual Test only | Andrew May + Tony Cowles |  | 230 |  |  | 99.9 | 0 |  | OK | Missing
A4 | MH Kitchen | Microwave Oven | 24 | 17.7.19 |  | Estimated use = 1h/week = 50h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | 13 | 0.05 | 99.9 | 1293 | 0.41 | OK | Pass
A34 | Stored here when not in use | Fairy Lights | 12 | 19.8.20 |  | Estimated use = .25h/week = 12h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | N/A | 99.9 | 7 |  | OK | Pass
A35 | Stored here when not in use | Fairy Light Timer | 12 | 19.8.20 |  | Estimated use = .25h/week = 12h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.02 | 99.9 |  |  | OK | Missing
A92 | Social room loft | Outside tree light | 12 | 19.8.20 |  | Estimated use = .25h/week = 12h/annun Suggest test every 2-3 years |  |  |  |  | N/A | 99.9 | 0 |  | OK | Pass
A93 | Social room loft | Outside tree light | 12 | 19.8.20 |  | Estimated use = .25h/week = 12h/annun Suggest test every 2-3 years |  |  |  |  | N/A | 99.9 | 0 |  | OK | Pass
A94 | Social room loft | Outside tree light | 12 | 19.8.20 |  | Estimated use = .25h/week = 12h/annun Suggest test every 2-3 years | [5 empty] | 99.9 | 0 |  |  | Missing
A95 | Social room loft | Outside tree light | 12 | 19.8.20 |  | Estimated use = .25h/week = 12h/annun Suggest test every 2-3 years | [5 empty] | 99.9 | 0 |  |  | Missing
A97 | Social room loft | Outside tree light 4 way adapter | 12 | 19.8.20 |  | Estimated use = .25h/week = 12h/annun Suggest test every 2-3 years |  |  |  |  | 0.06 | 99.9 |  |  | OK | Pass
A38 | Social Room Loft | Fairy Lights | 12 | 19.8.20 |  |  | Andrew May + Tony Cowles |  | 230 |  | N/A | 99.9 | 8 |  | OK | Pass
A40 | Social Room Loft | Fairy Lights | 12 | 19.8.20 |  | Estimated use = .25h/week = 12h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | N/A | 99.9 | 3 |  | OK | Pass
A41 | Social Room Loft | Fairy Lights | 12 | 19.8.20 |  | Visual Test Only | Andrew May + Tony Cowles |  | 230 |  | N/A | 99.9 | 13 |  | OK | Pass
A42 | Social Room Loft | 10 m Multiblock Extension | 12 | 19.8.20 |  | Estimated use = 2h/week = 100h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | 13 | 0.18 | 99.9 |  |  | OK | Missing
A43 | Social Room Loft | Fairy Lights | 12 | 19.8.20 |  | Estimated use = .25h/week = 12h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | N/A | 99.9 | 8 |  | OK | Pass
A32 | Chair store | portable hearing loop charger | 12 | 19.8.20 | [6 empty] | N/A | 99.9 | 7 |  | OK | Pass
A44 | Social Room Loft | Fairy Lights | 12 | 19.8.20 |  | Estimated use = .25h/week = 12h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | N/A | 99.9 | 5 |  | OK | Pass
A45 | Stage | Multiblock Extension | 12 | 19.8.20 |  | Estimated use = .25h/week = 12h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.01 | 999 |  |  | OK | Missing
A5 | MH Kitchen | Fridge | 24 | 17.7.19 |  | 24/7 - not moved - Suggest test every 2-3 years - Fixed Appliance | Andrew May + Tony Cowles |  | 230 | 13 | 0.12 | 99.9 | 0 | 0.12 | OK | Pass
A50 | Front of House Lighting Rail | New Acne Fresnel Spot | 36 | 24.5.17 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.01 | 999 |  |  | OK | Pass
A46 | Social Room Loft | Fairy Lights | 12 | 19.8.20 |  | Visual Test Only | Andrew May + Tony Cowles |  | 230 |  |  | 99.9 | 6 |  | OK | Pass
A52 | Front of House Lighting Rail | New Acne Fresnel Spot | 36 | 24.5.17 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.01 | 999 |  |  | OK | Pass
A53 | Front of House Lighting Rail | New Acne Fresnel Spot | 36 | 24.5.17 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.01 | 999 |  |  | OK | Pass
A54 | Front of House Lighting Rail | New Acne Fresnel Spot | 36 | 24.5.17 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.01 | 999 |  |  | OK | Pass
A55 | Front of House Lighting Rail | New Acne Fresnel Spot | 36 | 24.5.17 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.01 | 999 |  |  | OK | Pass
A56 | Front of House Lighting Rail | New Acne Fresnel Spot | 36 | 24.5.17 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.01 | 999 |  |  | OK | Pass
A57 | Front of House Lighting Rail | New Acne Fresnel Spot | 36 | 24.5.17 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.01 | 999 |  |  | OK | Pass
A58 | Front of House Lighting Rail | New Acne Fresnel Spot | 36 | 24.5.17 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.11 | 999 |  |  | OK | Pass
A59 | Front of House Lighting Rail | New Acne Fresnel Spot | 36 | 2013-11-06 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.06 | 999 |  |  | OK | Pass
A6 | MH Kitchen | Water Heater | 24 | 17.7.19 |  | On demand - say 100h/annun Suggest test every 2-3 years - Fixed Appliance | Andrew May + Tony Cowles |  | 230 | 3A | 0.07 | 99.9 | 19 | 0.7 | OK | Pass
A60 | Front of House Lighting Rail | Refurb Strand Profile Spot | 36 | 24.5.17 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.02 | 999 |  |  | OK | Pass
A61 | Front of House Lighting Rail | Refurb Strand Profile Spot | 36 | 24.5.17 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.11 | 999 |  |  | OK | Pass
A62 | Front of House Lighting Rail | Refurb Strand Profile Spot | 36 | 24.5.17 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.07 | 99.9 |  |  | OK | Pass
A63 | Front of House Lighting Rail | Refurb Strand Profile Spot | 36 | 24.5.17 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.05 | 999 |  |  | OK | Pass
A47 | Social Room Loft | Multiblock Extension | 12 | 21.6.18 |  | Removed from site 24/5/17 | Andrew May + Tony Cowles |  | 230 | [6 empty] | Missing
A48 | Lighting Loft | On Air Illuminated Sign | 24 | 21.6.18 |  |  | Andrew May + Tony Cowles |  | 230 |  | 99.9 | 99.9 | 113 |  |  | Pass
A49 | Social Room Loft | Multiblock Extension | 12 | 19.8.20 |  | Estimated use = 2h/week = 100h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 | 13 | 0.18 | 99.9 |  |  | OK | Missing
A51 | Front of House Lighting Rail | New Acme Fresnel Spot | 36 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.12 | 99.9 |  |  | OK | Pass
A64 | On-Stage | Refurb Strand Profile Spot | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.08 | 99.9 |  |  | OK | 2020 COVID postponed
A65 | On Stage | Refurb Strand Profile Spot | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.1 | 99.9 |  |  | OK | 2020 COVID postponed
A66 | On Stage | Refurb Strand Profile Spot | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.08 | 99.9 |  |  | OK | 2020 COVID postponed
A67 | Lighting Loft | Spare Refurb Strand Profile Spot | 36 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.07 | 99.9 |  |  | OK | Pass
A68 | Lighting Loft | Spare Refurb Strand Profile Spot | 36 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.08 | 99.9 |  |  | OK | Pass
A69 | Lighting Loft | Spare Refurb Strand Profile Spot | 36 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.01 | 999 |  |  | OK | Missing
A70 | Lighting Loft | Spare Refurb Strand Profile Spot | 36 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.04 | 999 |  |  | OK | Missing
A71 | On-Stage Lighting Rail | Refurb Black Box Fresnel Spot | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.08 | 99.9 |  |  | OK | 2020 COVID postponed
A72 | On Stage Lighting Rail | Refurb Black Box Fresnel Spot | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.08 | 99.9 |  |  | OK | 2020 COVID postponed
A73 | On Stage Lighting Rail | Refurb Black Box Fresnel Spot | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.08 | 99.9 |  |  | OK | 2020 COVID postponed
A74 | On Stage Lighting Rail | Refurb Black Box Fresnel Spot | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.08 | 99.9 |  |  | OK | 2020 COVID postponed
A75 | On Stage Lighting Rail | Refurb Black Box Fresnel Spot | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.09 | 99.9 |  |  | OK | 2020 COVID postponed
A76 | On Stage Lighting Rail | Refurb Black Box Fresnel Spot | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.08 | 99.9 |  |  | OK | 2020 COVID postponed
A77 | Lighting Loft | Spare Refurb Black Box Fresnel Spot | 36 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.09 | 99.9 |  |  | OK | Pass
A78 | Lighting Loft | Spare Refurb Black Box Fresnel Spot | 36 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.08 | 99.9 |  |  | OK | Pass
A79 | Lighting Loft | Spare Refurb Black Box Fresnel Spot | 36 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.08 | 99.9 |  |  | OK | Pass
A80 | Lighting Loft | Spare Strand Fresnel Spot | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.13 | 99.9 |  |  | OK | Pass
A81 | On Stage | Refurb Strand Fresnel Spot | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.11 | 99.9 |  |  | OK | 2020 COVID postponed
A82 | On Stage | Refurb Strand Fresnel Spot | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years | Andrew May + Tony Cowles |  | 230 |  | 0.14 | 99.9 |  |  | OK | 2020 COVID postponed
A83 | On-Stage | Compartment Battens | N/A | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years - Fixed Appliance | Andrew May + Tony Cowles |  | 230 |  | 0.08 | 99.9 |  |  | OK | Pass
A84 | On-Stage | Compartment Battens | N/A | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years - Fixed Appliance | Andrew May + Tony Cowles |  | 230 |  | 0.08 | 99.9 |  |  | OK | Pass
A85 | On-Stage | Compartment Battens | N/A | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years - Fixed Appliance | Andrew May + Tony Cowles |  | 230 |  | 0.08 | 99.9 |  |  | OK | Pass
A86 | On-Stage | Compartment Battens | N/A | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years - Fixed Appliance | Andrew May + Tony Cowles |  | 230 |  | 0.08 | 99.9 |  |  | OK | Pass
A87 | On-Stage | Compartment Battens | N/A | 21.6.18 |  | Numbered A9 on PAT Certificate - Fixed Appliance | Andrew May + Tony Cowles |  | 230 |  | 0.08 | 99.9 |  |  | OK | Pass
A88 | On-Stage | Compartment Battens | N/A | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years - Fixed Appliance | Andrew May + Tony Cowles |  | 230 |  | 0.09 | 99.9 |  |  | OK | Pass
A89 | On-Stage | Compartment Battens | N/A | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years - Fixed Appliance | Andrew May + Tony Cowles |  | 230 |  | 0.1 | 99.9 |  |  | OK | Pass
A90 | On-Stage | Compartment Battens | N/A | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years - Fixed Appliance | Andrew May + Tony Cowles |  | 230 |  | 0.1 | 99.9 |  |  | OK | Pass
A91 | On-Stage | Compartment Battens | N/A | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years - Fixed Appliance | Andrew May + Tony Cowles |  | 230 |  | 0.1 | 99.9 |  |  | OK | Pass
Equipment available for all RGVH user groups
Equipment Managed by All & Sundry Theatre Group
Equipment Originally used only by RG Players but since donated to RGVH
Form last updated 17.5.17. by Tony Cowles
PP 01 | Lighting Loft Patch Panel Cables | Cable from Lighting Loft to Lighting Rail | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years - Visual Test Only | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
PP 02 | Lighting Loft Patch Panel Cables | Cable from Lighting Loft to Lighting Rail | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years - Visual Test Only | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
PP 03 | Lighting Loft Patch Panel Cables | Cable from Lighting Loft to Lighting Rail | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years - Visual Test Only | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
PP 04 | Lighting Loft Patch Panel Cables | Cable from Lighting Loft to Lighting Rail | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years - Visual Test Only | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
PP 05 | Lighting Loft Patch Panel Cables | Cable from Lighting Loft to Lighting Rail | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years - Visual Test Only | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
PP 06 | Lighting Loft Patch Panel Cables | Cable from Lighting Loft to Lighting Rail | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years - Visual Test Only | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
PP 07 | Lighting Loft Patch Panel Cables | Cable from Lighting Loft to Lighting Rail | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years - Visual Test Only | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
PP 08 | Lighting Loft Patch Panel Cables | Cable from Lighting Loft to Lighting Rail | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years - Visual Test Only | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
PP 09 | Lighting Loft Patch Panel Cables | Cable from Lighting Loft to Lighting Rail | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years - Visual Test Only | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
PP 10 | Lighting Loft Patch Panel Cables | Cable from Lighting Loft to Lighting Rail | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years - Visual Test Only | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
PP 11 | Lighting Loft Patch Panel Cables | Cable from Lighting Loft to Lighting Rail | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years - Visual Test Only | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
PP 12 | Lighting Loft Patch Panel Cables | Cable from Lighting Loft to Lighting Rail | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years - Visual Test Only | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
PP 13 | Lighting Loft Patch Panel Cables | Cable from Lighting Loft to Lighting Rail | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years - Visual Test Only | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
PP 14 | Lighting Loft Patch Panel Cables | Cable from Lighting Loft to Lighting Rail | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years - Visual Test Only | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
PP 15 | Lighting Loft Patch Panel Cables | Cable from Lighting Loft to Lighting Rail | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years - Visual Test Only | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
PP 16 | Lighting Loft Patch Panel Cables | Cable from Lighting Loft to Lighting Rail | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years - Visual Test Only | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
PP 17 | Lighting Loft Patch Panel Cables | Cable from Lighting Loft to Lighting Rail | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years - Visual Test Only | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
PP 18 | Lighting Loft Patch Panel Cables | Cable from Lighting Loft to Lighting Rail | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years - Visual Test Only | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
PP 19 | Lighting Loft Patch Panel Cables | Cable from Lighting Loft to Lighting Rail | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years - Visual Test Only | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
PP 20 | Lighting Loft Patch Panel Cables | Cable from Lighting Loft to Lighting Rail | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years - Visual Test Only | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
PP 21 | Lighting Loft Patch Panel Cables | Cable from Lighting Loft to Lighting Rail | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years - Visual Test Only | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
PP 22 | Lighting Loft Patch Panel Cables | Cable from Lighting Loft to Lighting Rail | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years - Visual Test Only | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
PP 23 | Lighting Loft Patch Panel Cables | Cable from Lighting Loft to Lighting Rail | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years - Visual Test Only | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
PP 24 | Lighting Loft Patch Panel Cables | Cable from Lighting Loft to Lighting Rail | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years - Visual Test Only | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
PP 25 | Lighting Loft Patch Panel Cables | Cable from Lighting Loft to Lighting Rail | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years - Visual Test Only | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
PP 26 | Lighting Loft Patch Panel Cables | Cable from Lighting Loft to Lighting Rail | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years - Visual Test Only | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
PP 27 | Lighting Loft Patch Panel Cables | Cable from Lighting Loft to Lighting Rail | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years - Visual Test Only | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
PP 28 | Lighting Loft Patch Panel Cables | Cable from Lighting Loft to Lighting Rail | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years - Visual Test Only | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
PP 29 | Lighting Loft Patch Panel Cables | Cable from Lighting Loft to Lighting Rail | 24 | 21.6.18 |  | Estimated use = .4h/week = 20h/annun Suggest test every 2-3 years - Visual Test Only | Andrew May + Tony Cowles |  | 230 | [5 empty] | OK | Pass
A175 | Lighting Loft Extras | Desk Lamp | 12 | 17.7.19 | [7 empty] | 99.9 | 25 |  |  | Pass
A176 | Lighting Loft Extras | Radio Switch | 24 | 21.6.18 | [6 empty] | 0.01 | 99.9 |  |  |  | Pass
A177 | Lighting Loft Extras | Radio Switch | 24 | 21.6.18 | [6 empty] | 0.01 | 99.9 |  |  |  | Pass
A178 | Lighting Loft Extras | Radio Switch | 24 | 21.6.18 | [6 empty] | 0.01 | 99.9 |  |  |  | Pass
A179 | Lighting Loft Extras | Radio Switch | 24 | 21.6.18 | [6 empty] | 0.01 | 99.9 |  |  |  | Pass
A180 | Lighting Loft Extras | Overhead projector | 24 | 21.6.18 | [7 empty] | 99.7 | 387 |  |  | Pass
A181 | Lighting Loft Extras | Camera Power Supply | 12 | 21.6.18 |  | Not found 17.7.19 | [5 empty] | 99.9 | 0 |  |  | Not found
A182 | Lighting Loft Extras | LG Monitor | 24 | 21.6.18 | [6 empty] | 0.08 | 4.74 |  | 0.1 |  | Pass
A183 | Lighting Loft Extras | Mini Strobe | 12 | 21.6.18 |  | Fail, faulty power cable join with Asset A164 | [5 empty] | 99.9 | 5 |  |  | Fail
A184 | Lighting Loft Extras | Flash Box | 12 | 17.7.19 | [6 empty] | 0.16 | 99.9 |  |  |  | Pass
A185 | Lighting Loft | Acer Monitor Power Supply | 24 | 21.6.18 | [7 empty] | 99.9 | 6 |  |  | Pass
A186 | Lighting Loft | HP Desktop Computer | 24 | 21.6.18 | [6 empty] | 0.09 | 99.9 |  |  |  | Pass
A187 | Lighting Loft | Topaz Sound Desk | 24 | 21.6.18 | [7 empty] | 99.9 | 10 |  |  | Pass
A188 | Lighting Loft | Soundcraft Mixing desk | 24 | 21.6.18 | [7 empty] | 99.9 | 15 |  |  | Pass
A189 | Lighting Loft | Desk Lamp | 12 | 17.7.19 | [7 empty] | 99.9 | 25 |  |  | Pass
A190 | Lighting Loft | Extension Lead 1.5 m | 24 | 21.6.18 | [6 empty] | 0.05 | 99.9 |  |  |  | Pass
A191 | Lighting Loft | HDMI Booster | 24 | 21.6.18 | [7 empty] | 99.9 | 0 |  |  | Pass
A192 | Lighting Loft | Diversity Mic Receiver (no hassle) | 24 | 17.7.19 | [7 empty] | 99.9 | 0 |  |  | Pass
A193 | Lighting Loft | Foldback Speaker Amp | 24 | 21.6.18 | [7 empty] | 99.9 | 5 |  |  | Pass
A194 | Lighting Loft | Optiplex 760 Desktop PC | 24 | 21.6.18 | [6 empty] | 0.06 | 99.9 |  |  |  | Pass
A195 | Lighting Loft | Henry Vacuum Cleaner | 12 | 17.7.19 | [7 empty] | 99.9 | 1112 |  |  | Pass
A196 | Social Room Loft | Fairy Lights | 12 | 19.8.20 | [6 empty] | N/A | 99.9 | 0 |  |  | Pass
A197 | Social Room Loft | 2m Extension Lead | 12 | 19.8.20 | [11 empty] | Missing
A198 |  |  |  | 21.6.18
A199 |  |  |  | 21.6.18
A201 | Lighting loft | 4 way extension | 12 | 17.7.19 | [6 empty] | 0.06 | 99.9 |  |  |  | Pass
A204 | Social room loft | Fairy Light Transformer | 12 | 19.8.20 | [6 empty] | N/A | 99.9 | 10 |  |  | Pass
A205 | Social room loft | Fairy light transformer | 12 | 19.8.20 | [6 empty] | N/A | 99.9 | 9 |  |  | Pass
A206 | Social room loft | Short extension lead | 12 | 19.8.20 | [6 empty] | N/A | 99.9 | 0 |  |  | Pass
| MR Lobby | None | N/A
Chair Store
| Meeting Room | None
Social Room
| Rear Corridor Loft | None
Lighting Loft Patch Panel Cables
Note on A51: Tony Cowles: Changed to A181

## 2020 audit summary
2020 Audit summary
Due to COVID considerations the audit was limited to items in:
GROUND FLOOR GENERAL
SOCIAL ROOM LOFT
Items due for audit in Lighting Loft and Front of House Lighting Rail were postponed
Total Items tested as follows:
35 passed
3 added, tested and passed
8 missing
2 removed from testing (stage props)
1 removed from testing (off-site)
11 not tested due to COVID (stage lighting)
ITEMS ADDED
Asset ID | Location | Asset Description | Test Frequency |  | Last PAT test
A204 | Social room loft | Fairy Lights | 12 |  | 19.8.20
A205 | Social room loft | Fairy Lights | 12 |  | 19.8.20
A206 | Social room loft | Short extension lead | 12 |  | 19.8.20
ITEMS MISSING
Asset ID | Location | Asset Description | Test Frequency |  | Last PAT test
A94 | Social room loft | Outside tree light | 12 | 4 | 19.8.20
A95 | Social room loft | Outside tree light | 12 | 4 | 19.8.20
A42 | Social Room Loft | 10 m Multiblock Extension | 12 | 4 | 19.8.20
A49 | Social Room Loft | Multiblock Extension | 12 | 4 | 19.8.20
A197 | Social Room Loft | 2m Extension Lead | 12 | 4 | 19.8.20
A33 | Stored here when not in use | Fairy Lights | 12 | 1 | 17.7.19
A35 | Stored here when not in use | Fairy Light Timer | 12 | 1 | 21.6.18
A45 | Stage | Multiblock Extension | 12 | 1 | 21.6.18
ITEMS REMOVED FROM TESTING
Asset ID | Location | Asset Description | Test Frequency |  | Last PAT test | Reason for removal
A25 | Social Room Kitchen | Intempo Music Player | 12 | 1 | 21.6.18 | Off-site
A15 | SR Loft | Table Lamp | 24 | 4 | 19.8.20 | Stage prop only
A16 | SR Loft | Table Lamp | 24 | 4 | 19.8.20 | Stage prop only